OMNIstar-MIDI

Technical Product Specifications

Table of contents

1.	General Specifications	3

2.	Photometry	4

3.	Mechanics	6

4.	Electrical Characteristics	8

5.	Power Supply	8

6.	Environment	9

# General Specifications

| Product Description | The OMNISTAR has been designed to provide an unrivalled combination of performance and flexibility for lighting areas where high lumen packages are needed while offering maximum savings in energy and maintenance costs with a short payback time. This luminaire can be installed in various applications to provide the lighting distribution and lumen package needed to meet the specifications of the area to be lit. The OMNISTAR guarantees optimal lighting to ensure safety and comfort. It offers a real alternative to luminaires equipped with traditional sources, with the added advantages of an LED solution: low energy consumption, improved visibility with white light, limited maintenance, and longer life. The OMNISTAR is adaptable to all floodlighting applications to ensure maximum energy savings by adapting the light levels according to the needs. A wide range of photometry is available. The LensoFlex® photometric engine allows flexibility of multiple light distributions to ensure that the specific requirements of each application are met. ThermiX®: The OMNIstar offers an efficient thermal management of both the LEDs and the power supply thanks to the separation between the optical unit and the gear box. The cooling fins on the optical unit optimize the heat dissipation. This design enables the OMNIstar to perfectly manage high ambient temperatures (Ta up to 55°C) and ensures reliability in the long term. The luminaire housing is manufactured of high-pressure die-cast aluminum. To withstand even the most corrosive environments, the luminaire housing is especially e-coated (optional). This luminaire is available for emergency lighting, Zone 2 and 21/22 applications. It is designed for LED light sources between 136W and 226W. |
| --- | --- |
| Main applications | Industrial Areas - Highbay Industrial Warehouses Indoor Sports: Swimming pools, Gymnasium, Action Cricket, Soccer and Netball venues Outdoor Sport: Tennis Courts, Hockey Fields Transport hubs (airport aprons, harbours, bus stations and train stations) Streetlighting - large highway intersections, toll plazas Area Lighting |
| Recommended mounting height | 8 - 30m |

# Photometry

| Light source | LED |
| --- | --- |
| LED | 2mm2 or 4mm2 LED |
| Colour Temperature | 4000K (Neutral white 740) 5700K (Cool white 757) (optional) |
| Colour rendering (Ra) | ≥ 70 (Neutral white 740) ≥ 70 (Cool white 757) (optional) |
| LEDs / Wattage 60 LED @ 700mA 136W to 80 LEDs @900mA 226W | Lumen Package 20013lm to 32044lm |
| Optics | LensoFlex®4: 5304, 5304-W, 5355, 5356, 5366, 5405, 5407 BlastFlexTM4: 5357, 5357-W, 5358, 5359 |
| Photometry: |  |

|  | Lifetime residual flux Tq 250C |
| --- | --- |
| Number of LEDs | Neutral white (4000K) | 60 LEDs | 80 LEDs | 100.000h 90% |
| Current 700mA | Nominal Flux (lm) (1) | 20013 | - |  |
|  | Power Consumption (W) | 136 | - |  |
| Current 850mA | Nominal Flux (lm) (1) | - | 30043 |  |
|  | Power Consumption (W) | - | 212 |  |
| Current 900mA | Nominal Flux (lm) (1) | - | 32044 |  |
|  | Power Consumption (W) | - | 226 |  |
| Current 1000mA | Nominal Flux (lm) (1) | 25535 | - |  |
|  | Power Consumption (W) | 190 | - |  |

(1) The nominal flux is an indicative LED flux @ Ts 85°C based on LED manufacturer’s data. The real flux output of the luminaire depends on environmental conditions (e.g. temperature and pollution) and the optical efficiency of luminaire. The type of LED used is subject to change due to the ongoing rapid progress taking place in LED technology.

# Mechanics

| Electronic control Gear | Constant Current Driver |
| --- | --- |
| Materials and finishing | Housing Unpainted aluminium Protector – High Impact Clear Glass Optional: High-impact polycarbonate |
| Finish | Standard Pearl Light Grey (RAL 9022), Textured finish Optional: Any other RAL colour available on request |
| Installation | Standard: Stirrup version Optional: Suspended version U-bracket |
| Fixing | 2 x ø 8mm bolts (standard version) 4 x ø 6mm eyebolts (suspended version) |
| Weight (with gear) | Up to 10.8kg |
| Access | Yes |
| Aerodynamic resistance | 0.12m2 |

# Electrical Characteristics

| Line Voltage | 230VAC |
| --- | --- |
| Mains voltage Tolerance (AC) | 198-264V |
| Line frequency | 50Hz |
| Electrical Safety Class (IEC) | Class I |
| Surge protection | Yes - 10kV/10kA Optional - 20kV/20kA |
| Lighting control | Optional: 1-10V DALI Schréder ITERRA Schréder EXEDRA remote management 3-pin NEMA 7-pin NEMA |

# Power Supply

| Power Factor | ≥0.95 |
| --- | --- |
| Removable | Yes |
| Thermal Safety | Yes |

# Environment

| Storage temperature | - 400C to +600C |
| --- | --- |
| Operating temperature (Ta) | - 400C to + 500C |
| Enclosure Tightness | IP 66 |
| Enclosure Mechanical Withstand Impact | Up to IK 10 |

* Certified Test Standard SANS IEC 60598 -2-5 (available on request)

| Updated By: | Approved by | Document Revision / Date |
| --- | --- | --- |
| Nadja Smith | Pieter van Aardt | 05/04/2023 |

- For specific Tq, Ta and lifetime data, contact BEKA Schréder