BEKA VAPOURLINE

Technical Product Specifications

Table of contents

1.	General Specifications	3

2.	Photometry	4

3.	Mechanics	5

4.	Electrical Characteristics	6

5.	Power Supply	7

6.	Environment	7

- General Specifications

| Product Description | The Vapourline (VLN) luminaire consists of an injection-moulded, flame-retardant polycarbonate housing and prismatic diffuser. The powder coated white LED plate in the 4ft is secured into the diffuser that also houses the motion sensor; all other electrical components are mounted inside the housing, the diffuser clips securely onto the housing. The silicon sponge seal is moulded into the housing to ensure an optimal seal between the housing and the diffuser. A suspension hanger is provided to allow the easy installation of the fitting. It is designed to operate LEDs of up to 49W. The luminaire shall bear the SANS 60598-2-1 safety mark. The luminaire shall have a degree of protection that complies with SANS 60598-2-1: LED compartment: IP 65 The IP rating is supported by a certified SABS test report. The LED engine, consisting of the LED light source and the power supply. To maximize the reliability of the LED’s, the photometrical engine is completely sealed to IP 65. This ensures that the photometric performance is maintained over time. The IP65 rating is ensured by means of a silicon sponge gasket fixed into a groove to seal. The high-impact polycarbonate protector allows for impact resistance of IK 08. All control gear components are removable and bear the relevant Quality mark. All internal wiring are Teflon® coated to prevent damage by possible abrasion. The closing clips and all screws and metal parts are stainless steel or non-corrosive material. Mains connections by means of a suitable screw terminal block with a wire clamping contact. The luminaire power factor corrected to a minimum of 0,95. The IP 65 LED housing compartment optimizes the thermal operating environment around the LEDs enabling the long useful lifetime (60 000hrs, L70). With the introduction of LED technology Dimming options are much easier and further maximize energy savings. |
| --- | --- |
| Main applications | - Industry - Corrosive environments - Mining - Damp environments - Public buildings - Parking Garages |
| Recommended mounting height | 2m - 5m |

- Photometry

| Light source | LED |
| --- | --- |
| LED | Midpower |
| Light colour | 4000K (Neutral white 840) 5700K (Cool white 857) (optional) |
| Colour rendering (Ra) | ≥80 (Neutral white 840) ≥ 80 (Cool white 857) (optional) |
| Lumen package 27W 41W 49W | 4577lm 7122lm 8170lm |
| Optics | Symmetric |
| Photometry: |  |

| Description | LED Current | Lumen* | Lifetime Residual Flux @ tq 25°C |
| --- | --- | --- | --- |
|  |  |  | @60 000h |
| BEKA VLN 27W BEKA VLN 41W BEKA VLN 49W | 250mA 300mA 400mA | 4577 7122 8170 | 70% |

(*) The type of LED used is subject to change due to the ongoing rapid progress taking place in LED technology

- Mechanics

| Electronic control Gear | Constant Current LED Driver |
| --- | --- |
| Materials and finishing | Housing – High-impact Polycarbonate Protector – High-impact Polycarbonate |
| Coating | Light grey Polypropylene |
| Installation | Mounting clips |
| Fixing | Stainless steel mounting clips Mounting clips with suspension triangle |
| Dimensions (LxWxH) | 4ft: 1165 x 97 x 92* 5ft: 1573 x 101 x 101* *STD version |
| Weight (with gear) | 4ft: 2.1kg* 5ft: 2.5kg* *STD version |
| Access | Yes |
| Aerodynamic resistance (CxS): | N/A |

- Electrical Characteristics

| Line Voltage | 230VAC |
| --- | --- |
| Mains voltage Tolerance (AC) | 198-264V |
| Line frequency | 50Hz |
| Electrical Safety Class (IEC) | Class I |
| Surge protection | 10kV/10kA |
| Lighting control | Optional: DALI Movement sensor |

- Power Supply

| Power Factor | ≥0.95 |
| --- | --- |
| Removable | Yes |

- Environment

| Operating temperature | Standard version: -35 < T < 40deg C Emergency version: -35 < T < 35deg C |
| --- | --- |
| Enclosure Tightness | IP 65 |
| Enclosure Mechanical Withstand Impact | Polycarbonate – IK 08 |
| Enclosure Mechanical Withstand Vibrations | Modified IEC 60068-2-6 |
| Explosion proof | Zone 21/22 – (optional)(1) Zone 2 – (optional)(1) (1) Only available for the 30W & 41W versions |

| - Updated by | - Approved by | - Document Revision / Date |
| --- | --- | --- |
| - Nadja Smith | - Pieter van Aardt | - 13/02/2024 |

- For specific Tq, Ta and lifetime data, contact BEKA Schréder